GUIDELINES FOR INSTALLATION OF

TEMPORARY AND PERMANENT

ABOVEGROUND FUEL TANKS

LOCATED OUTSIDE OF BUILDINGS

Authority cited: California Fire Code

I.	General Information

These guidelines are applicable to the installation of aboveground tanks storing flammable and/or combustible liquids as fuel. The guidelines apply to both temporary and permanent tank installations. These guidelines are a supplement to other requirements and/or guidelines, and are not all-inclusive.

II.	Permits and Plans

- An installation permit is required from Planning and/or Building Department to install an aboveground motor vehicle fuel tank, an emergency or standby generator tank, piping, and associated equipment;

- A new or modified Hazardous Materials Business Plan (HMBP) is required before placing the tank(s) in service;

- Notification of the electric utility is required;

- Permits may also be required from the Ventura County Air Pollution Control District.

- Definitions

The following definitions apply with regard to requirements specified in this document:

Tank – A vessel containing more than 60 gallons.

Temporary Tank – A tank that is on-site no longer than thirty – (30) days.

Protected Aboveground Tank- is a listed tank system consisting of a primary tank provided with protection from physical damage, and fire – resistive protection from a high intensity liquid pool fire exposure. The tank system may provide these protection elements as a unit or may be an assembly of components.

# Quantity Limits

*Contact the local jurisdiction regarding installing tanks.

A.	Tanks

- Listing:  Each tank shall be designed and constructed in accordance with nationally recognized standards (UL 142/2244 or equivalent. UL 2085 is the listing for protected tanks). If it is not UL listed, provide documentation showing that it has been designed and constructed to a nationally recognized standard. (CFC §7902.1.8.1.1 & 7902.1.8.2.1)

- Separation Distances:  Each tank shall be separated from property lines, important buildings, public ways, and other tanks in accordance with CFC Table 7902.2-F, below:

TABLE 7902.2-F

Reference Table for Use In CFC Tables 7902.2-A, 7902.2-B and 7902.2-D

| Tank Capacity (gallons) | Minimum distance from property line of property which is or can be built upon, including the opposite side of a public way (feet) | Minimum distance from nearest side of any public way or from nearest important building on the same property (feet) |
| --- | --- | --- |
| 275 or less | 5 | 5 |
| 276 to 750 | 10 | 5 |
| 751 to 12,000 | 15 | 5 |
| 12,001 to 30,000 | 20 | 5 |

- Seismic Protection:  Seismic protection for tanks shall be provided in accordance with the Uniform Building Code. (CBC §1634.4)

(Exception: For temporary tanks, wheels may be chocked in lieu of providing seismic protection.)

- Vehicle Impact Protection:  Guard posts or other approved means shall be provided to protect tanks subject to vehicular damage.  When installed, posts shall be:  (CFC §7902.2.9)

- Constructed of steel not less than 4 inches in diameter and concrete filled;

- Spaced not more than 4 feet between posts on center;

- Set not less than 3 feet deep in a concrete footing of not less than 15 inches in diameter;

- Set with the top of the posts not less than 3 feet aboveground;

- Located not less than 5 feet from the tank.

(Note: For temporary tanks, K-rails or other substantial protection may be installed in lieu of guard posts.)

- Secondary Containment:  Tanks shall be provided with secondary containment (i.e. containment external to and separate from primary containment). Secondary containment shall be constructed of materials of sufficient thickness, density, and composition so as not to be structurally weakened as a result of contact with the fuel stored and capable of containing discharged fuel for a period of time equal to or longer than the maximum anticipated time sufficient to allow recovery of discharged fuel.  It shall be capable of containing 110% of the volume of the primary tank if a single tank is used, or in the case of multiple tanks, 150% of the largest tank or 10% of the aggregate, whichever is larger. If secondary containment is open to rainfall or sprinkler flow, contact the local jurisdiction for appropriate calculations.

- Spill Protection:  Spill containers shall be provided on top-filling and/or top-withdrawal connections.  Spill containers shall be non-combustible and shall be fixed to the tank.

- Spill Control:  Spill Control for hazardous materials liquid. Rooms, buildings or areas used for the storage of hazardous materials liquid in individual containers having a capacity of more than 55 gallons or when the aggregate of multiple containers exceeds 1000 gallons shall be provided with spill control or prevent the flow of liquids to adjoining areas. Floors in indoor locations and similar surfaces in outdoor locations shall be constructed to contain a spill from the largest single vessel

by one of the following methods:

- Liquid tight sloped or recessed floor in indoor locations or similar outdoor locations

- Liquid tight floors provided with liquid-tight raised sills or dikes or

- Sumps and collection systems.

Floors, sills, dikes and sumps shall be constructed of noncombustible material, and the liquid-tight seal shall be compatible with the material stored.

- Overfill Protection:  Tanks shall be provided with equipment to prevent overfilling as per the following table.

| Tank Size | Physical Situation | Approved Overfill Methods | Reference |
| --- | --- | --- | --- |
| < 500 gallons | Level of liquid in tank IS within sight of the operator and filling device IS within immediate control of operator | Visual observation |  |
| < 500 gallons | Level of liquid in tank is NOT within sight of the operator and/or filling device is NOT within immediate control of operator | High level (90%) alarm (with posted sign explaining alarm condition) Or Other liquid level limit control* |  |
| > 500 gallons | Any | Liquid level limit control | CFC §8001.4.8 |

*	A liquid level limit control is a mechanical or electronic device which physically limits the level of liquid in the tank (e.g. ball float or flapper valve in the fill line, dispenser nozzle shutoff, etc.).

B.	Piping Systems

- Support: Piping systems shall be substantially supported and protected against physical damage and excessive stresses arising from settlement, vibration, expansion or contraction, or exposure to fire. (CFC §7901.11.6)

- Seismic Protection:  Seismic protection for piping, tank supports and connections shall be provided in accordance with the Uniform Building Code.  (CFC §7902.1.10)

(Exception: Not normally required for temporary tanks.)

- Low Melting Point Materials:  For primary piping, low melting point materials such as aluminum, copper, and brass; materials, which soften on fire exposure such as non-metallic materials; or non-ductile materials such as cast iron, shall be within their pressure and temperature limitations.  When such materials are used, they shall be either:  (CFC §7901.11.1.2)

a.	Suitably protected against fire exposure; or

b.	Located such that leakage resulting from failure would not unduly expose persons, buildings, or structures; or

c.	Located where leakage can readily be controlled by operation of accessible remotely located valves.

- Vehicle Impact Protection:  Guard posts or other approved means shall be provided to protect piping, valves or fittings subject to vehicular damage.  When installed, posts shall be:  (CFC §7901.11.2)

a.	Constructed of steel not less than 4 inches in diameter and concrete filled;

b.	Spaced not more than 4 feet between posts on center;

c.	Set not less than 3 feet deep in a concrete footing of not less than 15 inches in diameter;

d.	Set with the top of the posts not less than 3 feet aboveground;

e.	Located not less than 5 feet from the tank.

(Note: For temporary tanks, K-rails or other substantial protection may be installed in lieu of guard posts.)

- Secondary Containment:  Supply and return piping shall be provided with secondary containment (i.e. containment external to and separate from primary containment).  Secondary containment shall be constructed of materials of sufficient thickness, density, and composition so as not to be structurally weakened as a result of contact with the fuel stored, and capable of containing discharged fuel for a period of time equal to or longer than the maximum anticipated time sufficient to allow recovery of discharged fuel. (Local Ordinance)

Potentially acceptable methods of containment include:

- Double-contained piping;

- Metal pan;

- Concrete berm;

- “Portable” berm (made of fuel-compatible materials);

- Containment enclosure.

- Connections:  Connections to a tank located below normal liquid level shall be provided with internal or external control valves located as close as practical to the shell of the tank.  When external, such valves, and their connections to the tank, shall be of steel.  (CFC §7901.11.5)

- Fill Pipe Length:  For tanks with a top-fill connection, metallic fill pipes shall terminate within 6 inches of the tank bottom to minimize static electricity. (CFC §7902.2.7.2)

- Filling/Withdrawal Connections:  Filling and withdrawal connections, which are made and broken, shall be located outside of buildings and not less than 5 feet from building openings. (CFC §7902.2.7.2)

- Normal Venting: Normal venting shall be provided for the primary tank as follows:

- The diameter of the normal vent opening shall be equal to the size of the fill/withdrawal opening, or at a minimum, 1-1/4 inch, whichever is greater.  (CFC §7902.1.11.8.1)

- Vapors shall be directed to discharge upward or horizontally away from closely adjacent walls, and the top of the vent shall be a minimum of 12 feet above adjacent ground level.  The vent opening shall be at least 5 feet from any building opening and/or property line.  (CFC §7902.1.11.4)

- Normal Vent Piping:  Vent pipes shall be installed such that they will drain toward the tank without sags or traps in which liquid can collect.  Vent pipes shall be installed such that they are not subject to physical damage or vibration. (CFC §7902.1.11.5)

- Emergency Venting:  Emergency venting shall be supplied as follows:

- Tanks shall be equipped with adequate additional venting that will relieve excessive internal pressure caused by exposure to fires. (CFC §7902.2.6.1)

- The pressure relief device shall not discharge inside a building. (CFC §7902.2.6.5.1)

(Note: for the purposes of emergency venting requirements, enclosures, which can be occupied, are considered buildings whereas enclosures, which cannot be occupied, are not considered buildings).

C.	Additional Requirements

1.	Security:  Storage, dispensing, use, and handling areas shall be secured against unauthorized entry and safeguarded with such protective facilities as public safety requires.  (CFC §8001.11.2)

2.	Electrical:  Electrical wiring and equipment shall be installed in accordance with the Electrical Code.  (CFC §8001.11.4)

- Monitoring:  Tank and piping secondary containment systems shall be monitored either visually or electronically. Monitoring shall occur at the low point of each secondary containment system. If electronic monitoring is used, it shall be connected to attention-getting visual and audible alarms. Contact your local agency for approved monitoring methods.

(Note: If response to monitoring alarms is hampered due to absence of site response personnel or there is a history of problems with alarm response at the site, the local agency may require shutdown of the generator during alarm activation.)

- Testing*:  Prior to being placed in service, tanks and associated piping shall be field tested in accordance with the following: (CFC §7901.11.10 & 7902.1.8.2.5)

|  | Field Test* | Duration |
| --- | --- | --- |
| Primary Tank Test | 5 p.s.i.g. | 30 minutes |
| Secondary Tank Test | 3 p.s.i.g. | 30 minutes |
| Primary Piping Test | Hydrostatically at 150% of anticipated pressure Or Pneumatically at 110% of anticipated pressure | 30 minutes |
| Secondary Piping Test | 5 p.s.i.g. | 30 minutes |

*	If the manufacturer’s specifications do not support the above testing procedures, follow the manufacturer’s recommended procedure.

5.	Hazardous Materials Signage and Labeling:  Warning and identification signs shall be posted to clearly identify hazards.   All piping shall be labeled.  (CFC §7901.9 & 7902.1.3.2)

- Additional Signage:  A sign shall be placed at the main electrical shut-off box identifying type and location of all normal and emergency power sources connected at that location. (CEC §702-8a)

- Fire Protection:  At least one 40:BC portable fire extinguisher shall be provided near and within sight of the equipment.  (UFC Standard 10-1)

- Access:  The required width of a fire apparatus access road (25’) shall not be obstructed in any manner, including the siting of generator/tank assemblies. (CFC §902.2.4.)

9. 	Spill Prevention Control and Countermeasure (SPCC) Plan: The owner or operator of any facility that stores more than 1,320 gallons of petroleum aboveground must prepare an SPCC Plan in accordance with guidelines contained in Part 112 of Title 40 of the Code of Federal Regulations.  Information regarding SPCC Plan preparation and submittal requirements is available on the Internet at www.swrcb.ca.gov/~cwphome/agt/index.htm. [HSC §2527005(c)]

(Exception:  Tank facilities located on a farm, nursery, logging site, or construction site are not required to prepare an SPCC Plan if no tank exceeds 20,000 gallons and cumulative storage capacity does not exceed 100,000 gallons.)

************************************************************************************

CFC Appendix 2F

1.	Flame Arresters:  Approved flame arresters shall be installed in normal vents. (CFC Appendix II-F §4.4.3)

2.	Projectile Protection:  When the chief requires a projectile test, the protected tank shall be tested in accordance with the requirements for bullet resistance. (CFC Appendix II-F, §4.5)

3.	Separation Distances:  Protected aboveground tanks shall be separated from property lines, important buildings, public ways, and other tanks in accordance with the following: (CFC Appendix II-F §5.1.1)

TABLE A-II-F-1

| Tank Capacity (gallons) | Minimum distance from property line of property which is or can be built upon, including the opposite side of a public way (feet) | Minimum distance from nearest side of any public way or from nearest important building on the same property (feet) | Minimum distance between tanks (feet) |
| --- | --- | --- | --- |
| Less than or equal to 6,000 | 15 | 5 | 3 |
| Greater than 6,000 | 25 | 15 | 3 |

4.	Aggregate Capacity:  Protected aboveground tank installations having the maximum allowable aggregate capacity shall be separated from other installations of protected aboveground tanks by not less than 100 feet. (CFC Appendix II-F §5.2)

5.	Overfill Prevention:  An overfill prevention system shall be provided for each tank as follows:

| Physical Situation | Approved Overfill Methods | Reference |
| --- | --- | --- |
| 85% of Tank Capacity | Audible or visual signal to notify tank filler; Or Tank level gauge marked at 85%; Or Other approved means. | CFC Appendix II-F §5.4 |
| 90% of Tank Capacity | Mechanical Shutoff Device | CFC Appendix II-F §5.4 |

6.	Filling Signage:  A permanent sign shall be provided at the fill point documenting the filling procedure and tank calibration chart.  The filling procedure shall require the person filling the tank to determine the gallonage required to fill it to 90% of capacity before commencing the fill operation. (CFC Appendix II-F §5.4)

7.	Spill Containment:  A spill container of not less than 5 gallons shall be provided for each fill connection.  For tanks with a remote fill connection, a portable spill container shall be provided.

(CFC Appendix II-F  §5.6)

8.	Anti-Siphon Devices:  Approved anti-siphon devices shall be installed in each external pipe connected to the tank when the pipe extends below the level of the top of the tank. (CFC Appendix II-F §6.4)